## TXF calc
| Inverter LF Toroid Transformer - Quick Calc. |  |  |  |  | Rev. 1.2
xxx | = input data
Silicone steel core
| Toroid |  |  |  | Ae Const. | 3100 | mm2 [for 1V/Turn ???]
Dia | 195 |  |  |  | Tr Const. | 8 | Turn Ratio for nom. 48V battery
Hole | 95 |  |  |  | Steel mass Const. | 7850 | kg/m3
Height | 90 |  |  |  | Density factor | 0.95 | (Lamination stacking)
[5 empty] | Battery | 24 | V nominal value
Section | 50 |  |  |  | RMS Out | 240 | V ac RMS
| 90 |  |  |  | Turn Ratio | 16
Hole area | 7088.2124 |  |  |  |  | 50
CS Area2 | 4500 | Ae
Core Volume | 2049889.2065 | mm3 |  |  | SiSteel Bmax Const. | 15000 | Gauss
Mass | 15.287
Volt/Turn | 1.4516 | Note 1
Sec. | 165.3333 | turn
Pri. | 10.3333 | turn |  | Note 1. This is not real V/T value ???
Bmax | 14530.6597 | Gauss
To be Reviewed & Checked
Toroid
[7 empty] | KeepItSimple | (if possible)
Following is not intended to be very accurate
Secondary Winding
Estimate…
| Wire dia. | 3.6 | mm
| Wire area | 10.1788 | mm2
| Wire offset | 1.5 | mm | <-- from core hole edge. (core Insulation + wire ctr line)
Sec. wire length
|  | 286 | mm per turn
|  | 47285.3333 | mm
|  | 0.084083 | Total resistance
| Wire fill | 1682.8869 | mm2
| Wire weight | 4.3125 | kg
|  | 10 | RMS
| Wire heat | 8.4083 | W
This calc only does 1 layer
| Const. 1mm2 = | 0.0181 | per m @25degC
| CU mass Const. | 8960 | kg/m3
50.0 mm
90.0 mm
Winding
ToniG 2023.02.19
95 mm
195 mm
This calc will likely have errors in method or formula.
It is intended to give results to evaluate a core that could then be confirmed with real testing.
4500 mm²
2049889 mm²

## Bmax from Turn
Bmax from secondary turns.
Data is from Sheet "TXF Calc" |  |  | xxx | = input data
[5 empty] | SiSteel Bmax Const. | 15000 | Gauss
Sec. | 170 | turn
Bmax | 14131.7788 | Gauss

## E-core Calc
Inverter LF Transformer Quick Calc |  |  |  | Rev. 0.90 |  | Silicone steel core
xxx | = input data |  |  |  | Toroid Ae Const. | 2800 | mm2 for 1V/Turn \
[5 empty] | Ecore Ae Const. | 2800 | " "
|  |  | E-core |  | Tr Const. | 8 | Turn Ratio for 48Vin
W.I.P. |  | Depth | 40 | mm | Steel mass Const. | 7850 | kg/m3
|  | Width | 50 | mm | Density factor | 0.9 | (Lamination stacking)
|  | Section | 40 |  | Battery | 24 | V
|  |  | 50 |  | RMS Out | 240
|  | CS Area2 | 2000 | Ae | Turn Ratio | 16
2(ctr leg only)
|  | Sec. | 336 | turn |  | This page Needs verifying & …
|  | Pri. | 21 | turn
E-core
40.0 mm
50.0 mm
Winding
ToniG 2023.02.07
2000.0 mm²

## Info
Notes:
For stacked identical cores, just add for the height.
Results are intended as a guide only, use realworld to validate.
Use to quickly evaluate a core.
Lamination stacking would include insulation & minute air gaps(core winding tightness & sheet dents will affect)
Rev. 1.0 2023.02.16 Toni.G
Compare results to known data & some info of available transformer.
Rev. 1.1 | 2023.02.18 TG
Add core hole area, secondary winding resistance.
Rev 1.2 | 2023.02.19 TG
Add Bmax calc